PURGENVENT Model 7930ECA

- 2.1	SPRINKLER SPECIALTY PIPE FITTINGS

Main Line Air Vent:

Product:  M7930ECA Automatic Air Venting Valve with End Cap. The Model 7930ECA includes an end cap so it is easily installed onto the end of branch lines with a coupling.

Standard:  UL's "Fire Protection Equipment Directory" listing or "Approval Guide," published by FM Global, listing.  NFPA 13, 13R, 13D (as applicable).

Includes M7900AAV.

Pressure Rating:  300 psig (2070 kPa).

End Cap:  Painted, Ductile Iron with Groove end and 1” NPT offset connection.

** NOTE TO SPECIFIER ** Delete inlet size not required.

Inlet Size:

2 inches (51 mm) Grooved end.

2.5 inches (64 mm) Grooved end.

3 inches (76 mm) Grooved end.

4 inches (102 mm) Grooved end.

6 inches (152 mm) Grooved end.

8 inches (203 mm) Grooved end.