- Model 3011A Inspector’s Test

- 2.1	SPRINKLER SPECIALTY PIPE FITTINGS

Sprinkler Inspector's Test Fittings:

Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

AGF Manufacturing Inc.; Model 3011A.

<Insert manufacturer's name>.

Standard:  UL's "Product iQ " listing or "Approval Guide," published by FM Global, listing.  NFPA 13, 13R, 13D as applicable.

Pressure Rating:  300 psig (2070 kPa).

Body Material: Bronze body, brass stem, steel handle, chrome-plated bronze ball, virgin teflon valve seat.

Components: A tamper resistant test orifice and a tapped port for system access.

Test Orifice Size:

** NOTE TO SPECIFIER **  Delete orifice size not required.

Nominal 2.8K (3/8 inch) , as required by NFPA 13, latest edition.

Nominal 4.2K (7/16 inch), as required by NFPA 13, latest edition.

Nominal 5.6K (1/2 inch), as required by NFPA 13, latest edition.

Nominal 8.0K (17/32 inch), as required by NFPA 13, latest edition.

Nominal 11.2K (5/8 inch,  ELO), as required by NFPA 13, latest edition.

Pressure Relief Valve and Drainage Piping:  AGF Model 7000

** NOTE TO SPECIFIER **  Delete pressure rating not required.

Pressure Rating:  Factory rated at 175 PSI.

Pressure Rating:  165 PSI.

Pressure Rating:  185 PSI.

Pressure Rating:  195 PSI.

Pressure Rating:  205 PSI.

Pressure Rating:  225 PSI.

Pressure Rating:  250 PSI.

Body Material:  Bronze body and stainless steel spring.

Components:  Nylobraid flexible tube, One 1/2 inch (13 mm) NPT by barbed 90 degree elbow, one ½” (13 mm) NPT by barbed straight adapter, external identification plate and integral flushing handle to remove debris

1/2 inch (13 mm) MIPT inlet, 1/2 inch (13 mm) FIPT outlet.

Relief pressure shall be factory set to project specifications.

Relief valve shall operate to the OPEN position between 90% and 105% of the set pressure.

Relief valve shall reseat or CLOSE at a minimum of 80% of set pressure.

Size: F.I.P.T., same as connected piping.

Inlet and Outlet: Threaded.