- Model 3011SG Inspector’s Test

- 2.1	SPRINKLER SPECIALTY PIPE FITTINGS

Sprinkler Inspector's Test Fittings:

Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

AGF Manufacturing Inc.; Model 3011SG.

<Insert manufacturer's name>.

Standard:  UL's "Product iQ " listing or "Approval Guide," published by FM Global, listing.  NFPA 13, 13R, 13D as applicable.

Pressure Rating:  300 psig (2070 kPa).

Body Material: Bronze body, brass stem, steel handle, chrome-plated bronze ball, virgin teflon valve seat.  Sight Glass: Bronze housing with viewing window.

Components: A tamper resistant test orifice and a tapped port for system access.

** NOTE TO SPECIFIER **  Delete orifice size not required.

Test Orifice Size:

Nominal 2.8K (3/8 inch) , as required by NFPA 13, latest edition.

Nominal 4.2K (7/16 inch), as required by NFPA 13, latest edition.

Nominal 5.6K (1/2 inch), as required by NFPA 13, latest edition.

Nominal 8.0K (17/32 inch), as required by NFPA 13, latest edition.

Nominal 11.2K (5/8 inch,  ELO), as required by NFPA 13, latest edition.

Size: F.I.P.T., same as connected piping.

Inlet and Outlet: Threaded.